# Kpower  MPF-90

# 12.8V 90Ah Group24 LiFePO4 Battery Datasheet

## Product Overview

This high-performance Lithium Iron Phosphate (LiFePO4) battery pack is designed for reliable and stable long-term operation. Encased in durable ABS material, it features a built-in BMS (Battery Management System) for comprehensive protection.

## Technical Specifications

| Category | Specification | Detail |
| --- | --- | --- |
| Model | Battery Model | MPF90 |
| Electrical | Nominal Voltage | 12.8V |
|  | Typical Capacity | 90Ah ± 2.7Ah (at 0.2C) |
|  | Cycle Life | ≥1000 cycles (≥80% capacity retention) |
| Discharge | Typical Current | 90A |
|  | Max Continuous Current | 300A |
|  | Peak Current | 800A (for 3 seconds) |
|  | Cut-off Voltage | ~10V |
| Charge | Charge Voltage | 14.4V ± 0.2V |
|  | Max Charging Current | 200A (for 60 seconds) |
|  | Charging Mode | Constant Current / Constant Voltage (CC/CV) |
| Physical | Dimensions (LWH) | 10.24 × 6.61 × 8.23 in |
|  | Weight | 25.5 LB |
|  | Terminals | M8 Terminal |
|  | Case Material | ABS |

## Operating Environment

- Charge Temperature: 0°C to +55°C

- Discharge Temperature: -20°C to +60°C

- Storage Temperature: -20°C to +45°C (up to 3 months); optimal at 15°C to 25°C

- Environmental Humidity: ≤85% RH

## Integrated Protection Features

The built-in BMS provides safety monitoring for:

- Overcharge and Over-discharge

- Over-current and Short circuit

- Temperature protection

## Dealer Maintenance & Storage Guidelines

- Storage Maintenance: Charge and discharge the battery pack once every 2 months to prevent over-discharge. Maintain voltage between 13.28V and 13.6V during storage.

- Installation: Install in a well-ventilated, dry, and clean environment. Ensure terminal polarities are correct to avoid fire or equipment damage.

- Usage Tip: Shallow charging and discharging (discharging to 80% of nominal capacity) is recommended to improve overall cycle life.